## Sheet1
|  | Buffer: |  |  | 1.2255
|  | multiplying factor: |  |  | 6 | [6 empty] | COST OF MODEL / Year
| Hour | Load Demand (kW) | Load Demand with Buffer (kW) | kw production | multiplying factor | Array Output (kW) | Battery Charging | Battery charge spread out | Generator Energy Demand | Generator Output (kW) | Generator running? | Buffer: | 1.2255
| 0 | 278.4 | 341.1792 | 0 | 6 | 0 | 0 | 41.88 | 299.2992 | 299.2992 | 1 | Multiplying factor | 6 |  |  | #CONSTNATS |  | unit
| 1 | 276.2 | 338.4831 | 0 | 6 | 0 | 0 | 41.88 | 296.6031 | 296.6031 | 1
| 2 | 274.1 | 335.9096 | 0 | 6 | 0 | 0 | 41.88 | 294.0296 | 294.0296 | 1 | Equipment |  |  |  | #Battery Specs
| 3 | 271 | 332.1105 | 0 | 6 | 0 | 0 | 41.88 | 290.2305 | 290.2305 | 1 | Cost of panel | 227700 |  |  | battery_capacity = | 13.5 | kW | Number of batteries | 32
| 4 | 269.3 | 330.0272 | 0 | 6 | 0 | 0 | 41.88 | 288.1472 | 288.1472 | 1 | Cost of batteries | 272000 |  |  | battery_cost = | 8500 | $
| 5 | 279.7 | 342.7724 | 2.2333 | 6 | 13.4 | 0 | 0 | 329.3724 | 329.3724 | 1 | Cost of controller | 450 |  |  | battery_maintenance = | 50 | $/year
| 6 | 311.8 | 382.1109 | 12.3 | 6 | 73.8 | 0 | 0 | 308.3109 | 308.3109 | 1 | cost of generator | 0 |  |  | battery_dc_voltage = | 50 | V
| 7 | 299.3 | 366.7922 | 30.45 | 6 | 182.7 | 0 | 0 | 184.0922 | 184.0922 | 1
| 8 | 302.3 | 370.4687 | 48.9833 | 6 | 293.9 | 0 | 0 | 76.5687 | 76.5687 | 1
| 9 | 313.2 | 383.8266 | 61.9 | 6 | 371.4 | 58.2 | 0 | -45.7734 | 0 | 0 | Operating Costs
| 10 | 321.3 | 393.7532 | 69.475 | 6 | 416.85 | 95.55 | 0 | -118.6469 | 0 | 0 | Solar | 10350 |  |  | #Solar Panel Specs
| 11 | 322.5 | 395.2237 | 73.275 | 6 | 439.65 | 117.15 | 0 | -161.5762 | 0 | 0 | Battery | 1600 |  |  | panel_cost = | 220 | $ | Number of panels | 1035
| 12 | 345 | 422.7975 | 72.275 | 6 | 433.65 | 88.65 | 0 | -99.5025 | 0 | 0 | Generator Fuel | 135371.2 |  |  | panel_maintenance = | 10 | $/year
| 13 | 336.7 | 412.6259 | 65.9917 | 6 | 395.95 | 59.25 | 0 | -42.5741 | 0 | 0 | Generator Maintenance | 18000 |  |  | panel_wattage = | 0.425 | kW
| 14 | 329.1 | 403.3121 | 54.0917 | 6 | 324.55 | 0 | 0 | 78.7621 | 78.7621 | 1 |  |  |  |  | efficiency = | 0.9
| 15 | 325.5 | 398.9003 | 36.7583 | 6 | 220.55 | 0 | 0 | 178.3503 | 178.3503 | 1
| 16 | 315.9 | 387.1354 | 16.8 | 6 | 100.8 | 0 | 0 | 286.3354 | 286.3354 | 1 | Initial Cost | 500150 | 4584371 | 0 | #Inverter Specs
| 17 | 318.3 | 390.0767 | 4.225 | 6 | 25.35 | 0 | 0 | 364.7267 | 364.7267 | 1 | Cost/Year | 165321.2 | 59080 | 144490.94 | inverter_cost = | 0 | $ | Number of inverters
| 18 | 328.1 | 402.0866 | 0.94167 | 6 | 5.65 | 0 | 0 | 396.4366 | 396.4366 | 1 |  |  |  |  | inverter_maintenance = | 0 | $
| 19 | 364.6 | 446.8173 | 0 | 6 | 0 | 0 | 41.88 | 404.9373 | 404.9373 | 1
| 20 | 339.9 | 416.5474 | 0 | 6 | 0 | 0 | 41.88 | 374.6674 | 374.6674 | 1 |  |  |  |  | #Charge Controller Specs
| 21 | 315.6 | 386.7678 | 0 | 6 | 0 | 0 | 41.88 | 344.8878 | 344.8878 | 1 |  |  |  |  | controller_cost = | 15 | $ | Number of controllers | 30
| 22 | 308.1 | 377.5766 | 0 | 6 | 0 | 0 | 41.88 | 335.6966 | 335.6966 | 1 | TOTAL | 4741052.083 | 6099920.7 | 3706553.8383 | controller_maintenance = | 5 | $
| 23 | 288.1 | 353.0666 | 0 | 6 | 0 | 0 | 41.88 | 311.1866 | 311.1866 | 1 |  |  |  |  | controller_amperage = | 30 | A
| TOTAL ENERGY | 7434 | 9110.367 | 549.7 | 144 | 3298.2 | 418.8 |  | 4974.567 | 5442.6402 | [5 empty] | #Generators
[16 empty] | Generator cost | 40000 | $ | Number of generators | 12
[9 empty] | Max Generator Demand | 404.9373 | 19 |  |  |  |  | Generator maintenance | 1500 | $ | (full capacity)
[16 empty] | Fuel/year | 42748.8
|  | Cost Comparison | [13 empty] | Fuel rate (gallons/hour) | 4.88 | gallons/hour
|  | Multiplying factor |  | Initial Cost | Cost/year | Total operation cost for 25 years |  |  | Total Cost of Trial for 25 years | [6 empty] | cost of fuel | 4 | $/gallon
No solar or battery |  | 0 |  | 0 | 425275.2 | 10909372.068 |  |  | 5309944.37 | [6 empty] | Number of hour Generator is operating | 19 | hours
|  | 10 |  | 1791235 | 148546.8 | 5601831.787 |  |  | 7541613.587 | [6 empty] | Hours/year | 6935
|  | 20 |  | 5418250 | 157614 | 9461443.135 |  |  | 15037307.135
|  | 30 |  | 9172765 | 160014.4 | 13277534.396 |  |  | 22610313.796
|  | 40 |  | 12961280 | 197304.4 | 18022631.121 |  |  | 31181215.521
|  | 50 |  | 16758295 | 354100.94 | 25841869.3634 |  |  | 42954265.3034
|  | 60 |  | 2055310 | 271984.4 | 9032389.821 |  |  | 11359684.221
|  | 70 |  | 24343810 | 309274.4 | 32277471.546 |  |  | 56930555.946
|  | 80 |  | 28157825 | 346714.4 | 37051916.146 |  |  | 65556455.546
|  | 90 |  | 31972060 | 366819 | 41381884.3975 |  |  | 73720763.3975
|  | 100 |  | 35794575 | 404309 | 46166111.6225 |  |  | 82364995.6225
|  | 110 |  | 39617090 | 441799.6 | 50950354.239 |  |  | 91009243.839
|  | 120 |  | 43439605 | 479289.6 | 55734581.464 |  |  | 99653476.064
|  | 130 |  | 47270620 | 516829.6 | 60528591.314 |  |  | 108316040.914
|  | 135 |  | 49186120 | 535599 | 62925573.3475 |  |  | 112647292.3475
|  |  | Multiplying Factor | Total
|  |  | 0 | 5309944.37
|  |  | 1 | 5392458.19
|  |  | 2 | 5474495.49
|  |  | 3 | 5557009.32
|  |  | 4 | 5639046.62
|  |  | 5 | 5607269.89
|  |  | 6 | 5202797.08
|  |  | 7 | 5232340.52
|  |  | 8 | 5637680.97
|  |  | 9 | 6042529.89
|  |  | 10 | 6294449.29
All solar and battery, no generator